## INDEX
Teadit Torque Calculation and Bolt Stress Check
Select the desired Dimensional Units:
METRIC
IMPERIAL

## IMPERIAL
Torque Calculation and Bolt Stress Check for Packing Installation
| Valve |  |  |  |  | Packing Style:
| Stem Diameter [in] |  |  | Required Torque
| Packing Cross-Section [in] |  |  |  | Recommended Torque
| Number of Bolts |  |  |  | Acceptable for "General Service Valves" **
| Media Pressure [psi] |  |  |  | Minimum Value for "General Service Valves" **
Bolt
% of Bolt Max. Yield
| Bolt Grade/Material |  |  |  | Maximum Bolt Yield Stress
| Bolt Class |  | 1 |  | Acceptable for "General Service Valves" **
| Bolt Diameter [in] |  |  |  | Minimum Value for "General Service Valves" **
| "k" Factor |  | 0.16
TORQUE WRENCHES MUST BE USED
* Certified Low-Emissions
(1.) Established protocol is essential and must be maintained
** General Service
(1.) Targeted torque Certified Low Emissions service is goal. However, yielding of equipment is not recommended to achieve this value. A "Compression Set" for the packing is the desired effect.
(2.) At least 50% of the torque value of "Valves Certified Low Emission Service" is necessary to achieve success with 2236 as a General Service packing. Bolting capable of delivering calculated torque values must be used. Adjust k-factor in formula to match thread lubricant used.
(3.) 50% of initial preload ("General Service Minimum Suggested Value") is delivered to equipment.
(4.) If 50% initial preload is not achievable without yielding equipment, consultation with Teadit Engineering is required.
(5.) Equipment is checked to see if cycling is achievable, compressing the first ring in the process.
(6.) If cycling is possible, increase torque value to 60% of initial preload, compressing the second ring in the process. Check to see if cycling is achievable.
(7.) If cycling is possible at 60%, increase torque value to 70% ("Acceptable for General Service Valves"), compressing the third ring in the process. Check to see if cycling is achievable.
(8.) If cycling is possible at 70%, continue with the same process for rings 4 and 5. If cycling is not possible, revert to 60%, and continue with rings 4 and 5.
(9.) Equipment must be allowed to relax, as per LE protocol, 3 to 5 days. At this time, a retightening at the same finish value in Step 8 is performed.
HOME
CLEAR
PRINT

## METRIC
Torque Calculation and Bolt Stress Check for Packing Installation
| Valve | [5 empty] | Packing Style:
| Stem Diameter [mm] |  |  |  | Required Torque
| Packing Cross-Section [mm] |  |  |  |  | Recommended Torque
| Number of Bolts |  |  |  |  | Acceptable for "General Service Valves" **
| Media Pressure [bar] |  |  |  |  | Minimum Value for "General Service Valves" **
Bolt
% of Bolt Max. Yield
| Bolt Grade/Material |  |  |  |  | Maximum Bolt Yield Stress
| Bolt Class |  | 1 |  |  | Acceptable for "General Service Valves" **
| Bolt Diameter [mm] |  |  | #N/A |  | Minimum Value for "General Service Valves" **
| "k" Factor |  | 0.16
TORQUE WRENCHES MUST BE USED
* Certified Low-Emissions
(1.) Established protocol is essential and must be maintained
** General Service
(1.) Targeted torque Certified Low Emissions service is goal. However, yielding of equipment is not recommended to achieve this value. A "Compression Set" for the packing is the desired effect.
(2.) At least 50% of the torque value of "Valves Certified Low Emission Service" is necessary to achieve success with 2236 as a General Service packing. Bolting capable of delivering calculated torque values must be used. Adjust k-factor in formula to match thread lubricant used.
(3.) 50% of initial preload ("General Service Minimum Suggested Value") is delivered to equipment.
(4.) If 50% initial preload is not achievable without yielding equipment, consultation with Teadit Engineering is required.
(5.) Equipment is checked to see if cycling is achievable, compressing the first ring in the process.
(6.) If cycling is possible, increase torque value to 60% of initial preload, compressing the second ring in the process. Check to see if cycling is achievable.
(7.) If cycling is possible at 60%, increase torque value to 70% ("Acceptable for General Service Valves"), compressing the third ring in the process. Check to see if cycling is achievable.
(8.) If cycling is possible at 70%, continue with the same process for rings 4 and 5. If cycling is not possible, revert to 60%, and continue with rings 4 and 5.
(9.) Equipment must be allowed to relax, as per LE protocol, 3 to 5 days. At this time, a retightening at the same finish value in Step 8 is performed.
HOME
CLEAR
PRINT

## DATA (hidden)
1
| Aux | Grade | Diameter [in] | Class | Yield Stress [ksi] | Grade/Material List |  | Sealing Confidence Level |  |  | Class 1/2 |  | Class List
| 651A0,251 | 651A | 0.25 | 1 | 60 | 651A |  | 1 | 35 | 5076.288 | B8 |  | 1
| 651A0,31251 | 651A | 0.3125 | 1 | 60 | 651B |  | 2 | 45 | 6526.656 | B8C |  | 2
| 651A0,3751 | 651A | 0.375 | 1 | 60 | 660A |  | 3 | 55 | 7977.024 | B8M
| 651A0,43751 | 651A | 0.4375 | 1 | 60 | 660B |  | 4 | 65 | 9427.392 | B8T
| 651A0,51 | 651A | 0.5 | 1 | 60 | B16 |  | 5 | 73 | 10587.6864
| 651A0,56251 | 651A | 0.5625 | 1 | 60 | B4B
| 651A0,6251 | 651A | 0.625 | 1 | 60 | B4C |  | Root and Tensile Stress Area |  |  | Packing 'y' [MPa] |  |  | Imperial [psi] | Metric [MPa]
| 651A0,751 | 651A | 0.75 | 1 | 60 | B5 |  | Diameter [in] | Root [in²] | Tensile [in²] |  | 0 |  | #N/A | #N/A
| 651A0,8751 | 651A | 0.875 | 1 | 60 | B6 |  | 0.25 | 0.0269 | 0.0318 | 2000IC | 35
| 651A11 | 651A | 1 | 1 | 60 | B7 |  | 0.3125 | 0.0454 | 0.0524 | 2000S | 25 |  | Torque Recommendation
| 651A1,1251 | 651A | 1.125 | 1 | 60 | B7M |  | 0.375 | 0.0678 | 0.0775 | 2005FDA | 25 |  | Recommended for "Certified Low Emission" Valves *
| 651A1,251 | 651A | 1.25 | 1 | 60 | B8 |  | 0.4375 | 0.0933 | 0.1063 | 2202 | 20 |  | Acceptable for "General Service Valves" **
| 651A1,3751 | 651A | 1.375 | 1 | 60 | B8C |  | 0.5 | 0.1257 | 0.1419 | 2235 | 55 |  | Minimum Value for "General Service Valves" **
| 651A1,51 | 651A | 1.5 | 1 | 60 | B8F |  | 0.5625 | 0.162 | 0.182 | 2236 | 73
| 651A1,6251 | 651A | 1.625 | 1 | 60 | B8M |  | 0.625 | 0.2017 | 0.226 | 2237 | 73
| 651A1,751 | 651A | 1.75 | 1 | 60 | B8T |  | 0.75 | 0.3019 | 0.3345 | 2005R | 4
| 651A1,8751 | 651A | 1.875 | 1 | 60 | BC |  | 0.875 | 0.4192 | 0.4617
| 651A21 | 651A | 2 | 1 | 60 | BD |  | 1 | 0.5509 | 0.6057
| 651A2,251 | 651A | 2.25 | 1 | 60 | L43 |  | 1.125 | 0.7276 | 0.7905
| 651A2,51 | 651A | 2.5 | 1 | 60 | L7 |  | 1.25 | 0.9289 | 0.9997
| 651A2,751 | 651A | 2.75 | 1 | 60 | L7A |  | 1.375 | 1.155 | 1.234
| 651A31 | 651A | 3 | 1 | 70 | L7B |  | 1.5 | 1.405 | 1.492
| 651A3,251 | 651A | 3.25 | 1 | 70 | L7C |  | 1.625 | 1.68 | 1.775
| 651A3,51 | 651A | 3.5 | 1 | 70 | L7M |  | 1.75 | 1.979 | 2.082
| 651A3,751 | 651A | 3.75 | 1 | 70 | 3.6 |  | 1.875 | 2.303 | 2.414
| 651A41 | 651A | 4 | 1 | 70 | 4.6 |  | 2 | 2.652 | 2.771
| 651B0,251 | 651B | 0.25 | 1 | 50 | 4.8 |  | 2.25 | 3.422 | 3.557
| 651B0,31251 | 651B | 0.3125 | 1 | 50 | 5.6 |  | 2.5 | 4.291 | 4.442
| 651B0,3751 | 651B | 0.375 | 1 | 50 | 5.8 |  | 2.75 | 5.258 | 5.425
| 651B0,43751 | 651B | 0.4375 | 1 | 50 | 6.8 |  | 3 | 6.324 | 6.506
| 651B0,51 | 651B | 0.5 | 1 | 50 | 8.8 |  | 3.25 | 7.487 | 7.686
| 651B0,56251 | 651B | 0.5625 | 1 | 50 | 9.8 |  | 3.5 | 8.748 | 8.963
| 651B0,6251 | 651B | 0.625 | 1 | 50 | 10.9 |  | 3.75 | 10.11 | 10.34
| 651B0,751 | 651B | 0.75 | 1 | 50 | 12.9 |  | 4 | 11.57 | 11.81
| 651B0,8751 | 651B | 0.875 | 1 | 50 | A2/A4-70
| 651B11 | 651B | 1 | 1 | 50 | 25CrMo4 |  | Dia. Metric | Rt. [mm²] | Tensile [mm²]
| 651B1,1251 | 651B | 1.125 | 1 | 50 | 42CrMo4 |  | M14-2 | 102.1 | 115.4
| 651B1,251 | 651B | 1.25 | 1 | 50 | I718 |  | M16-2 | 141 | 156.7
| 651B1,3751 | 651B | 1.375 | 1 | 50 |  |  | M20-2.5 | 220.4 | 244.8
| 651B1,51 | 651B | 1.5 | 1 | 50 |  |  | M24-3 | 317.3 | 352.5
| 651B1,6251 | 651B | 1.625 | 1 | 50 |  |  | M27-3 | 419.1 | 459.4
| 651B1,751 | 651B | 1.75 | 1 | 50 |  |  | M30-3 | 535 | 580.4
| 651B1,8751 | 651B | 1.875 | 1 | 50 |  |  | M33-3 | 665.1 | 715.6
| 651B21 | 651B | 2 | 1 | 50 |  |  | M36-3 | 809.3 | 864.9
| 651B2,251 | 651B | 2.25 | 1 | 50 |  |  | M39-3 | 976.6 | 1028
| 651B2,51 | 651B | 2.5 | 1 | 50 |  |  | M42-3 | 1140 | 1206
| 651B2,751 | 651B | 2.75 | 1 | 50 |  |  | M45-3 | 1327 | 1398
| 651B31 | 651B | 3 | 1 | 60 |  |  | M48-3 | 1527 | 1604
| 651B3,251 | 651B | 3.25 | 1 | 60 |  |  | M52-3 | 1817 | 1900
| 651B3,51 | 651B | 3.5 | 1 | 60 |  |  | M56-3 | 2132 | 2222
| 651B3,751 | 651B | 3.75 | 1 | 60 |  |  | M64-3 | 2837 | 2940
| 651B41 | 651B | 4 | 1 | 60 |  |  | M70-3 | 3432 | 3545
| 660A0,251 | 660A | 0.25 | 1 | 85 |  |  | M76-3 | 4083 | 4207
| 660A0,31251 | 660A | 0.3125 | 1 | 85 |  |  | M82-3 | 4791 | 4925
| 660A0,3751 | 660A | 0.375 | 1 | 85 |  |  | M90-3 | 5822 | 5970
| 660A0,43751 | 660A | 0.4375 | 1 | 85 |  |  | M95-3 | 6518 | 6674
| 660A0,51 | 660A | 0.5 | 1 | 85 |  |  | M100-3 | 7253 | 7418
| 660A0,56251 | 660A | 0.5625 | 1 | 85
| 660A0,6251 | 660A | 0.625 | 1 | 85
| 660A0,751 | 660A | 0.75 | 1 | 85
| 660A0,8751 | 660A | 0.875 | 1 | 85
| 660A11 | 660A | 1 | 1 | 85
| 660A1,1251 | 660A | 1.125 | 1 | 85
| 660A1,251 | 660A | 1.25 | 1 | 85
| 660A1,3751 | 660A | 1.375 | 1 | 85
| 660A1,51 | 660A | 1.5 | 1 | 85
| 660A1,6251 | 660A | 1.625 | 1 | 85
| 660A1,751 | 660A | 1.75 | 1 | 85
| 660A1,8751 | 660A | 1.875 | 1 | 85
| 660A21 | 660A | 2 | 1 | 85
| 660A2,251 | 660A | 2.25 | 1 | 85
| 660A2,51 | 660A | 2.5 | 1 | 85
| 660A2,751 | 660A | 2.75 | 1 | 85
| 660A31 | 660A | 3 | 1 | 85
| 660A3,251 | 660A | 3.25 | 1 | 85
| 660A3,51 | 660A | 3.5 | 1 | 85
| 660A3,751 | 660A | 3.75 | 1 | 85
| 660A41 | 660A | 4 | 1 | 85
| 660B0,251 | 660B | 0.25 | 1 | 85
| 660B0,31251 | 660B | 0.3125 | 1 | 85
| 660B0,3751 | 660B | 0.375 | 1 | 85
| 660B0,43751 | 660B | 0.4375 | 1 | 85
| 660B0,51 | 660B | 0.5 | 1 | 85
| 660B0,56251 | 660B | 0.5625 | 1 | 85
| 660B0,6251 | 660B | 0.625 | 1 | 85
| 660B0,751 | 660B | 0.75 | 1 | 85
| 660B0,8751 | 660B | 0.875 | 1 | 85
| 660B11 | 660B | 1 | 1 | 85
| 660B1,1251 | 660B | 1.125 | 1 | 85
| 660B1,251 | 660B | 1.25 | 1 | 85
| 660B1,3751 | 660B | 1.375 | 1 | 85
| 660B1,51 | 660B | 1.5 | 1 | 85
| 660B1,6251 | 660B | 1.625 | 1 | 85
| 660B1,751 | 660B | 1.75 | 1 | 85
| 660B1,8751 | 660B | 1.875 | 1 | 85
| 660B21 | 660B | 2 | 1 | 85
| 660B2,251 | 660B | 2.25 | 1 | 85
| 660B2,51 | 660B | 2.5 | 1 | 85
| 660B2,751 | 660B | 2.75 | 1 | 85
| 660B31 | 660B | 3 | 1 | 85
| 660B3,251 | 660B | 3.25 | 1 | 85
| 660B3,51 | 660B | 3.5 | 1 | 85
| 660B3,751 | 660B | 3.75 | 1 | 85
| 660B41 | 660B | 4 | 1 | 85
| B160,251 | B16 | 0.25 | 1 | 105
| B160,31251 | B16 | 0.3125 | 1 | 105
| B160,3751 | B16 | 0.375 | 1 | 105
| B160,43751 | B16 | 0.4375 | 1 | 105
| B160,51 | B16 | 0.5 | 1 | 105
| B160,56251 | B16 | 0.5625 | 1 | 105
| B160,6251 | B16 | 0.625 | 1 | 105
| B160,751 | B16 | 0.75 | 1 | 105
| B160,8751 | B16 | 0.875 | 1 | 105
| B1611 | B16 | 1 | 1 | 105
| B161,1251 | B16 | 1.125 | 1 | 105
| B161,251 | B16 | 1.25 | 1 | 105
| B161,3751 | B16 | 1.375 | 1 | 105
| B161,51 | B16 | 1.5 | 1 | 105
| B161,6251 | B16 | 1.625 | 1 | 105
| B161,751 | B16 | 1.75 | 1 | 105
| B161,8751 | B16 | 1.875 | 1 | 105
| B1621 | B16 | 2 | 1 | 105
| B162,251 | B16 | 2.25 | 1 | 105
| B162,51 | B16 | 2.5 | 1 | 105
| B162,751 | B16 | 2.75 | 1 | 95
| B1631 | B16 | 3 | 1 | 95
| B163,251 | B16 | 3.25 | 1 | 95
| B163,51 | B16 | 3.5 | 1 | 95
| B163,751 | B16 | 3.75 | 1 | 95
| B1641 | B16 | 4 | 1 | 95
| B4B0,251 | B4B | 0.25 | 1 | 105
| B4B0,31251 | B4B | 0.3125 | 1 | 105
| B4B0,3751 | B4B | 0.375 | 1 | 105
| B4B0,43751 | B4B | 0.4375 | 1 | 105
| B4B0,51 | B4B | 0.5 | 1 | 105
| B4B0,56251 | B4B | 0.5625 | 1 | 105
| B4B0,6251 | B4B | 0.625 | 1 | 105
| B4B0,751 | B4B | 0.75 | 1 | 105
| B4B0,8751 | B4B | 0.875 | 1 | 105
| B4B11 | B4B | 1 | 1 | 105
| B4B1,1251 | B4B | 1.125 | 1 | 105
| B4B1,251 | B4B | 1.25 | 1 | 105
| B4B1,3751 | B4B | 1.375 | 1 | 105
| B4B1,51 | B4B | 1.5 | 1 | 105
| B4B1,6251 | B4B | 1.625 | 1 | 105
| B4B1,751 | B4B | 1.75 | 1 | 105
| B4B1,8751 | B4B | 1.875 | 1 | 105
| B4B21 | B4B | 2 | 1 | 105
| B4B2,251 | B4B | 2.25 | 1 | 105
| B4B2,51 | B4B | 2.5 | 1 | 105
| B4B2,751 | B4B | 2.75 | 1 | 105
| B4B31 | B4B | 3 | 1 | 105
| B4B3,251 | B4B | 3.25 | 1 | 105
| B4B3,51 | B4B | 3.5 | 1 | 105
| B4B3,751 | B4B | 3.75 | 1 | 105
| B4B41 | B4B | 4 | 1 | 105
| B4C0,251 | B4C | 0.25 | 1 | 85
| B4C0,31251 | B4C | 0.3125 | 1 | 85
| B4C0,3751 | B4C | 0.375 | 1 | 85
| B4C0,43751 | B4C | 0.4375 | 1 | 85
| B4C0,51 | B4C | 0.5 | 1 | 85
| B4C0,56251 | B4C | 0.5625 | 1 | 85
| B4C0,6251 | B4C | 0.625 | 1 | 85
| B4C0,751 | B4C | 0.75 | 1 | 85
| B4C0,8751 | B4C | 0.875 | 1 | 85
| B4C11 | B4C | 1 | 1 | 85
| B4C1,1251 | B4C | 1.125 | 1 | 85
| B4C1,251 | B4C | 1.25 | 1 | 85
| B4C1,3751 | B4C | 1.375 | 1 | 85
| B4C1,51 | B4C | 1.5 | 1 | 85
| B4C1,6251 | B4C | 1.625 | 1 | 85
| B4C1,751 | B4C | 1.75 | 1 | 85
| B4C1,8751 | B4C | 1.875 | 1 | 85
| B4C21 | B4C | 2 | 1 | 85
| B4C2,251 | B4C | 2.25 | 1 | 85
| B4C2,51 | B4C | 2.5 | 1 | 85
| B4C2,751 | B4C | 2.75 | 1 | 85
| B4C31 | B4C | 3 | 1 | 85
| B4C3,251 | B4C | 3.25 | 1 | 85
| B4C3,51 | B4C | 3.5 | 1 | 85
| B4C3,751 | B4C | 3.75 | 1 | 85
| B4C41 | B4C | 4 | 1 | 85
| B50,251 | B5 | 0.25 | 1 | 100
| B50,31251 | B5 | 0.3125 | 1 | 100
| B50,3751 | B5 | 0.375 | 1 | 100
| B50,43751 | B5 | 0.4375 | 1 | 100
| B50,51 | B5 | 0.5 | 1 | 100
| B50,56251 | B5 | 0.5625 | 1 | 100
| B50,6251 | B5 | 0.625 | 1 | 100
| B50,751 | B5 | 0.75 | 1 | 100
| B50,8751 | B5 | 0.875 | 1 | 100
| B511 | B5 | 1 | 1 | 100
| B51,1251 | B5 | 1.125 | 1 | 100
| B51,251 | B5 | 1.25 | 1 | 100
| B51,3751 | B5 | 1.375 | 1 | 100
| B51,51 | B5 | 1.5 | 1 | 100
| B51,6251 | B5 | 1.625 | 1 | 100
| B51,751 | B5 | 1.75 | 1 | 100
| B51,8751 | B5 | 1.875 | 1 | 100
| B521 | B5 | 2 | 1 | 100
| B52,251 | B5 | 2.25 | 1 | 100
| B52,51 | B5 | 2.5 | 1 | 100
| B52,751 | B5 | 2.75 | 1 | 100
| B531 | B5 | 3 | 1 | 100
| B53,251 | B5 | 3.25 | 1 | 100
| B53,51 | B5 | 3.5 | 1 | 100
| B53,751 | B5 | 3.75 | 1 | 100
| B541 | B5 | 4 | 1 | 100
| B60,251 | B6 | 0.25 | 1 | 85
| B60,31251 | B6 | 0.3125 | 1 | 85
| B60,3751 | B6 | 0.375 | 1 | 85
| B60,43751 | B6 | 0.4375 | 1 | 85
| B60,51 | B6 | 0.5 | 1 | 85
| B60,56251 | B6 | 0.5625 | 1 | 85
| B60,6251 | B6 | 0.625 | 1 | 85
| B60,751 | B6 | 0.75 | 1 | 85
| B60,8751 | B6 | 0.875 | 1 | 85
| B611 | B6 | 1 | 1 | 85
| B61,1251 | B6 | 1.125 | 1 | 85
| B61,251 | B6 | 1.25 | 1 | 85
| B61,3751 | B6 | 1.375 | 1 | 85
| B61,51 | B6 | 1.5 | 1 | 85
| B61,6251 | B6 | 1.625 | 1 | 85
| B61,751 | B6 | 1.75 | 1 | 85
| B61,8751 | B6 | 1.875 | 1 | 85
| B621 | B6 | 2 | 1 | 85
| B62,251 | B6 | 2.25 | 1 | 85
| B62,51 | B6 | 2.5 | 1 | 85
| B62,751 | B6 | 2.75 | 1 | 85
| B631 | B6 | 3 | 1 | 85
| B63,251 | B6 | 3.25 | 1 | 85
| B63,51 | B6 | 3.5 | 1 | 85
| B63,751 | B6 | 3.75 | 1 | 85
| B641 | B6 | 4 | 1 | 85
| B70,251 | B7 | 0.25 | 1 | 105
| B70,31251 | B7 | 0.3125 | 1 | 105
| B70,3751 | B7 | 0.375 | 1 | 105
| B70,43751 | B7 | 0.4375 | 1 | 105
| B70,51 | B7 | 0.5 | 1 | 105
| B70,56251 | B7 | 0.5625 | 1 | 105
| B70,6251 | B7 | 0.625 | 1 | 105
| B70,751 | B7 | 0.75 | 1 | 105
| B70,8751 | B7 | 0.875 | 1 | 105
| B711 | B7 | 1 | 1 | 105
| B71,1251 | B7 | 1.125 | 1 | 105
| B71,251 | B7 | 1.25 | 1 | 105
| B71,3751 | B7 | 1.375 | 1 | 105
| B71,51 | B7 | 1.5 | 1 | 105
| B71,6251 | B7 | 1.625 | 1 | 105
| B71,751 | B7 | 1.75 | 1 | 105
| B71,8751 | B7 | 1.875 | 1 | 105
| B721 | B7 | 2 | 1 | 105
| B72,251 | B7 | 2.25 | 1 | 105
| B72,51 | B7 | 2.5 | 1 | 105
| B72,751 | B7 | 2.75 | 1 | 95
| B731 | B7 | 3 | 1 | 95
| B73,251 | B7 | 3.25 | 1 | 95
| B73,51 | B7 | 3.5 | 1 | 95
| B73,751 | B7 | 3.75 | 1 | 95
| B741 | B7 | 4 | 1 | 95
| B7M0,251 | B7M | 0.25 | 1 | 80
| B7M0,31251 | B7M | 0.3125 | 1 | 80
| B7M0,3751 | B7M | 0.375 | 1 | 80
| B7M0,43751 | B7M | 0.4375 | 1 | 80
| B7M0,51 | B7M | 0.5 | 1 | 80
| B7M0,56251 | B7M | 0.5625 | 1 | 80
| B7M0,6251 | B7M | 0.625 | 1 | 80
| B7M0,751 | B7M | 0.75 | 1 | 80
| B7M0,8751 | B7M | 0.875 | 1 | 80
| B7M11 | B7M | 1 | 1 | 80
| B7M1,1251 | B7M | 1.125 | 1 | 80
| B7M1,251 | B7M | 1.25 | 1 | 80
| B7M1,3751 | B7M | 1.375 | 1 | 80
| B7M1,51 | B7M | 1.5 | 1 | 80
| B7M1,6251 | B7M | 1.625 | 1 | 80
| B7M1,751 | B7M | 1.75 | 1 | 80
| B7M1,8751 | B7M | 1.875 | 1 | 80
| B7M21 | B7M | 2 | 1 | 80
| B7M2,251 | B7M | 2.25 | 1 | 80
| B7M2,51 | B7M | 2.5 | 1 | 80
| B7M2,751 | B7M | 2.75 | 1 | 80
| B7M31 | B7M | 3 | 1 | 80
| B7M3,251 | B7M | 3.25 | 1 | 80
| B7M3,51 | B7M | 3.5 | 1 | 80
| B7M3,751 | B7M | 3.75 | 1 | 80
| B7M41 | B7M | 4 | 1 | 80
| B80,251 | B8 | 0.25 | 1 | 30
| B80,31251 | B8 | 0.3125 | 1 | 30
| B80,3751 | B8 | 0.375 | 1 | 30
| B80,43751 | B8 | 0.4375 | 1 | 30
| B80,51 | B8 | 0.5 | 1 | 30
| B80,56251 | B8 | 0.5625 | 1 | 30
| B80,6251 | B8 | 0.625 | 1 | 30
| B80,751 | B8 | 0.75 | 1 | 30
| B80,8751 | B8 | 0.875 | 1 | 30
| B811 | B8 | 1 | 1 | 30
| B81,1251 | B8 | 1.125 | 1 | 30
| B81,251 | B8 | 1.25 | 1 | 30
| B81,3751 | B8 | 1.375 | 1 | 30
| B81,51 | B8 | 1.5 | 1 | 30
| B81,6251 | B8 | 1.625 | 1 | 30
| B81,751 | B8 | 1.75 | 1 | 30
| B81,8751 | B8 | 1.875 | 1 | 30
| B821 | B8 | 2 | 1 | 30
| B82,251 | B8 | 2.25 | 1 | 30
| B82,51 | B8 | 2.5 | 1 | 30
| B82,751 | B8 | 2.75 | 1 | 30
| B831 | B8 | 3 | 1 | 30
| B83,251 | B8 | 3.25 | 1 | 30
| B83,51 | B8 | 3.5 | 1 | 30
| B83,751 | B8 | 3.75 | 1 | 30
| B841 | B8 | 4 | 1 | 30
| B80,252 | B8 | 0.25 | 2 | 100
| B80,31252 | B8 | 0.3125 | 2 | 100
| B80,3752 | B8 | 0.375 | 2 | 100
| B80,43752 | B8 | 0.4375 | 2 | 100
| B80,52 | B8 | 0.5 | 2 | 100
| B80,56252 | B8 | 0.5625 | 2 | 100
| B80,6252 | B8 | 0.625 | 2 | 100
| B80,752 | B8 | 0.75 | 2 | 100
| B80,8752 | B8 | 0.875 | 2 | 65
| B812 | B8 | 1 | 2 | 65
| B81,1252 | B8 | 1.125 | 2 | 65
| B81,252 | B8 | 1.25 | 2 | 65
| B81,3752 | B8 | 1.375 | 2 | 50
| B81,52 | B8 | 1.5 | 2 | 50
| B81,6252 | B8 | 1.625 | 2 | 80
| B81,752 | B8 | 1.75 | 2 | 80
| B81,8752 | B8 | 1.875 | 2 | 80
| B822 | B8 | 2 | 2 | 80
| B82,252 | B8 | 2.25 | 2 | 80
| B82,52 | B8 | 2.5 | 2 | 80
| B82,752 | B8 | 2.75 | 2 | 80
| B832 | B8 | 3 | 2 | 80
| B83,252 | B8 | 3.25 | 2 | 80
| B83,52 | B8 | 3.5 | 2 | 80
| B83,752 | B8 | 3.75 | 2 | 80
| B842 | B8 | 4 | 2 | 80
| B8C0,251 | B8C | 0.25 | 1 | 30
| B8C0,31251 | B8C | 0.3125 | 1 | 30
| B8C0,3751 | B8C | 0.375 | 1 | 30
| B8C0,43751 | B8C | 0.4375 | 1 | 30
| B8C0,51 | B8C | 0.5 | 1 | 30
| B8C0,56251 | B8C | 0.5625 | 1 | 30
| B8C0,6251 | B8C | 0.625 | 1 | 30
| B8C0,751 | B8C | 0.75 | 1 | 30
| B8C0,8751 | B8C | 0.875 | 1 | 30
| B8C11 | B8C | 1 | 1 | 30
| B8C1,1251 | B8C | 1.125 | 1 | 30
| B8C1,251 | B8C | 1.25 | 1 | 30
| B8C1,3751 | B8C | 1.375 | 1 | 30
| B8C1,51 | B8C | 1.5 | 1 | 30
| B8C1,6251 | B8C | 1.625 | 1 | 30
| B8C1,751 | B8C | 1.75 | 1 | 30
| B8C1,8751 | B8C | 1.875 | 1 | 30
| B8C21 | B8C | 2 | 1 | 30
| B8C2,251 | B8C | 2.25 | 1 | 30
| B8C2,51 | B8C | 2.5 | 1 | 30
| B8C2,751 | B8C | 2.75 | 1 | 30
| B8C31 | B8C | 3 | 1 | 30
| B8C3,251 | B8C | 3.25 | 1 | 30
| B8C3,51 | B8C | 3.5 | 1 | 30
| B8C3,751 | B8C | 3.75 | 1 | 30
| B8C41 | B8C | 4 | 1 | 30
| B8C0,252 | B8C | 0.25 | 2 | 100
| B8C0,31252 | B8C | 0.3125 | 2 | 100
| B8C0,3752 | B8C | 0.375 | 2 | 100
| B8C0,43752 | B8C | 0.4375 | 2 | 100
| B8C0,52 | B8C | 0.5 | 2 | 100
| B8C0,56252 | B8C | 0.5625 | 2 | 100
| B8C0,6252 | B8C | 0.625 | 2 | 100
| B8C0,752 | B8C | 0.75 | 2 | 100
| B8C0,8752 | B8C | 0.875 | 2 | 65
| B8C12 | B8C | 1 | 2 | 65
| B8C1,1252 | B8C | 1.125 | 2 | 65
| B8C1,252 | B8C | 1.25 | 2 | 65
| B8C1,3752 | B8C | 1.375 | 2 | 50
| B8C1,52 | B8C | 1.5 | 2 | 50
| B8C1,6252 | B8C | 1.625 | 2 | 80
| B8C1,752 | B8C | 1.75 | 2 | 80
| B8C1,8752 | B8C | 1.875 | 2 | 80
| B8C22 | B8C | 2 | 2 | 80
| B8C2,252 | B8C | 2.25 | 2 | 80
| B8C2,52 | B8C | 2.5 | 2 | 80
| B8C2,752 | B8C | 2.75 | 2 | 80
| B8C32 | B8C | 3 | 2 | 80
| B8C3,252 | B8C | 3.25 | 2 | 80
| B8C3,52 | B8C | 3.5 | 2 | 80
| B8C3,752 | B8C | 3.75 | 2 | 80
| B8C42 | B8C | 4 | 2 | 80
| B8F0,251 | B8F | 0.25 | 1 | 30
| B8F0,31251 | B8F | 0.3125 | 1 | 30
| B8F0,3751 | B8F | 0.375 | 1 | 30
| B8F0,43751 | B8F | 0.4375 | 1 | 30
| B8F0,51 | B8F | 0.5 | 1 | 30
| B8F0,56251 | B8F | 0.5625 | 1 | 30
| B8F0,6251 | B8F | 0.625 | 1 | 30
| B8F0,751 | B8F | 0.75 | 1 | 30
| B8F0,8751 | B8F | 0.875 | 1 | 30
| B8F11 | B8F | 1 | 1 | 30
| B8F1,1251 | B8F | 1.125 | 1 | 30
| B8F1,251 | B8F | 1.25 | 1 | 30
| B8F1,3751 | B8F | 1.375 | 1 | 30
| B8F1,51 | B8F | 1.5 | 1 | 30
| B8F1,6251 | B8F | 1.625 | 1 | 30
| B8F1,751 | B8F | 1.75 | 1 | 30
| B8F1,8751 | B8F | 1.875 | 1 | 30
| B8F21 | B8F | 2 | 1 | 30
| B8F2,251 | B8F | 2.25 | 1 | 30
| B8F2,51 | B8F | 2.5 | 1 | 30
| B8F2,751 | B8F | 2.75 | 1 | 30
| B8F31 | B8F | 3 | 1 | 30
| B8F3,251 | B8F | 3.25 | 1 | 30
| B8F3,51 | B8F | 3.5 | 1 | 30
| B8F3,751 | B8F | 3.75 | 1 | 30
| B8F41 | B8F | 4 | 1 | 30
| B8M0,251 | B8M | 0.25 | 1 | 30
| B8M0,31251 | B8M | 0.3125 | 1 | 30
| B8M0,3751 | B8M | 0.375 | 1 | 30
| B8M0,43751 | B8M | 0.4375 | 1 | 30
| B8M0,51 | B8M | 0.5 | 1 | 30
| B8M0,56251 | B8M | 0.5625 | 1 | 30
| B8M0,6251 | B8M | 0.625 | 1 | 30
| B8M0,751 | B8M | 0.75 | 1 | 30
| B8M0,8751 | B8M | 0.875 | 1 | 30
| B8M11 | B8M | 1 | 1 | 30
| B8M1,1251 | B8M | 1.125 | 1 | 30
| B8M1,251 | B8M | 1.25 | 1 | 30
| B8M1,3751 | B8M | 1.375 | 1 | 30
| B8M1,51 | B8M | 1.5 | 1 | 30
| B8M1,6251 | B8M | 1.625 | 1 | 30
| B8M1,751 | B8M | 1.75 | 1 | 30
| B8M1,8751 | B8M | 1.875 | 1 | 30
| B8M21 | B8M | 2 | 1 | 30
| B8M2,251 | B8M | 2.25 | 1 | 30
| B8M2,51 | B8M | 2.5 | 1 | 30
| B8M2,751 | B8M | 2.75 | 1 | 30
| B8M31 | B8M | 3 | 1 | 30
| B8M3,251 | B8M | 3.25 | 1 | 30
| B8M3,51 | B8M | 3.5 | 1 | 30
| B8M3,751 | B8M | 3.75 | 1 | 30
| B8M41 | B8M | 4 | 1 | 30
| B8M0,252 | B8M | 0.25 | 2 | 95
| B8M0,31252 | B8M | 0.3125 | 2 | 95
| B8M0,3752 | B8M | 0.375 | 2 | 95
| B8M0,43752 | B8M | 0.4375 | 2 | 95
| B8M0,52 | B8M | 0.5 | 2 | 95
| B8M0,56252 | B8M | 0.5625 | 2 | 95
| B8M0,6252 | B8M | 0.625 | 2 | 95
| B8M0,752 | B8M | 0.75 | 2 | 95
| B8M0,8752 | B8M | 0.875 | 2 | 65
| B8M12 | B8M | 1 | 2 | 65
| B8M1,1252 | B8M | 1.125 | 2 | 65
| B8M1,252 | B8M | 1.25 | 2 | 65
| B8M1,3752 | B8M | 1.375 | 2 | 50
| B8M1,52 | B8M | 1.5 | 2 | 50
| B8M1,6252 | B8M | 1.625 | 2 | 80
| B8M1,752 | B8M | 1.75 | 2 | 80
| B8M1,8752 | B8M | 1.875 | 2 | 80
| B8M22 | B8M | 2 | 2 | 80
| B8M2,252 | B8M | 2.25 | 2 | 80
| B8M2,52 | B8M | 2.5 | 2 | 80
| B8M2,752 | B8M | 2.75 | 2 | 80
| B8M32 | B8M | 3 | 2 | 80
| B8M3,252 | B8M | 3.25 | 2 | 80
| B8M3,52 | B8M | 3.5 | 2 | 80
| B8M3,752 | B8M | 3.75 | 2 | 80
| B8M42 | B8M | 4 | 2 | 80
| B8T0,251 | B8T | 0.25 | 1 | 30
| B8T0,31251 | B8T | 0.3125 | 1 | 30
| B8T0,3751 | B8T | 0.375 | 1 | 30
| B8T0,43751 | B8T | 0.4375 | 1 | 30
| B8T0,51 | B8T | 0.5 | 1 | 30
| B8T0,56251 | B8T | 0.5625 | 1 | 30
| B8T0,6251 | B8T | 0.625 | 1 | 30
| B8T0,751 | B8T | 0.75 | 1 | 30
| B8T0,8751 | B8T | 0.875 | 1 | 30
| B8T11 | B8T | 1 | 1 | 30
| B8T1,1251 | B8T | 1.125 | 1 | 30
| B8T1,251 | B8T | 1.25 | 1 | 30
| B8T1,3751 | B8T | 1.375 | 1 | 30
| B8T1,51 | B8T | 1.5 | 1 | 30
| B8T1,6251 | B8T | 1.625 | 1 | 30
| B8T1,751 | B8T | 1.75 | 1 | 30
| B8T1,8751 | B8T | 1.875 | 1 | 30
| B8T21 | B8T | 2 | 1 | 30
| B8T2,251 | B8T | 2.25 | 1 | 30
| B8T2,51 | B8T | 2.5 | 1 | 30
| B8T2,751 | B8T | 2.75 | 1 | 30
| B8T31 | B8T | 3 | 1 | 30
| B8T3,251 | B8T | 3.25 | 1 | 30
| B8T3,51 | B8T | 3.5 | 1 | 30
| B8T3,751 | B8T | 3.75 | 1 | 30
| B8T41 | B8T | 4 | 1 | 30
| B8T0,252 | B8T | 0.25 | 2 | 100
| B8T0,31252 | B8T | 0.3125 | 2 | 100
| B8T0,3752 | B8T | 0.375 | 2 | 100
| B8T0,43752 | B8T | 0.4375 | 2 | 100
| B8T0,52 | B8T | 0.5 | 2 | 100
| B8T0,56252 | B8T | 0.5625 | 2 | 100
| B8T0,6252 | B8T | 0.625 | 2 | 100
| B8T0,752 | B8T | 0.75 | 2 | 100
| B8T0,8752 | B8T | 0.875 | 2 | 65
| B8T12 | B8T | 1 | 2 | 65
| B8T1,1252 | B8T | 1.125 | 2 | 65
| B8T1,252 | B8T | 1.25 | 2 | 65
| B8T1,3752 | B8T | 1.375 | 2 | 50
| B8T1,52 | B8T | 1.5 | 2 | 50
| B8T1,6252 | B8T | 1.625 | 2 | 80
| B8T1,752 | B8T | 1.75 | 2 | 80
| B8T1,8752 | B8T | 1.875 | 2 | 80
| B8T22 | B8T | 2 | 2 | 80
| B8T2,252 | B8T | 2.25 | 2 | 80
| B8T2,52 | B8T | 2.5 | 2 | 80
| B8T2,752 | B8T | 2.75 | 2 | 80
| B8T32 | B8T | 3 | 2 | 80
| B8T3,252 | B8T | 3.25 | 2 | 80
| B8T3,52 | B8T | 3.5 | 2 | 80
| B8T3,752 | B8T | 3.75 | 2 | 80
| B8T42 | B8T | 4 | 2 | 80
| BC0,251 | BC | 0.25 | 1 | 99
| BC0,31251 | BC | 0.3125 | 1 | 99
| BC0,3751 | BC | 0.375 | 1 | 99
| BC0,43751 | BC | 0.4375 | 1 | 99
| BC0,51 | BC | 0.5 | 1 | 99
| BC0,56251 | BC | 0.5625 | 1 | 99
| BC0,6251 | BC | 0.625 | 1 | 99
| BC0,751 | BC | 0.75 | 1 | 99
| BC0,8751 | BC | 0.875 | 1 | 99
| BC11 | BC | 1 | 1 | 99
| BC1,1251 | BC | 1.125 | 1 | 99
| BC1,251 | BC | 1.25 | 1 | 99
| BC1,3751 | BC | 1.375 | 1 | 99
| BC1,51 | BC | 1.5 | 1 | 99
| BC1,6251 | BC | 1.625 | 1 | 99
| BC1,751 | BC | 1.75 | 1 | 99
| BC1,8751 | BC | 1.875 | 1 | 99
| BC21 | BC | 2 | 1 | 99
| BC2,251 | BC | 2.25 | 1 | 99
| BC2,51 | BC | 2.5 | 1 | 99
| BC2,751 | BC | 2.75 | 1 | 99
| BC31 | BC | 3 | 1 | 99
| BC3,251 | BC | 3.25 | 1 | 99
| BC3,51 | BC | 3.5 | 1 | 99
| BC3,751 | BC | 3.75 | 1 | 99
| BC41 | BC | 4 | 1 | 99
| BD0,251 | BD | 0.25 | 1 | 130
| BD0,31251 | BD | 0.3125 | 1 | 130
| BD0,3751 | BD | 0.375 | 1 | 130
| BD0,43751 | BD | 0.4375 | 1 | 130
| BD0,51 | BD | 0.5 | 1 | 130
| BD0,56251 | BD | 0.5625 | 1 | 130
| BD0,6251 | BD | 0.625 | 1 | 130
| BD0,751 | BD | 0.75 | 1 | 130
| BD0,8751 | BD | 0.875 | 1 | 130
| BD11 | BD | 1 | 1 | 130
| BD1,1251 | BD | 1.125 | 1 | 130
| BD1,251 | BD | 1.25 | 1 | 130
| BD1,3751 | BD | 1.375 | 1 | 130
| BD1,51 | BD | 1.5 | 1 | 130
| BD1,6251 | BD | 1.625 | 1 | 130
| BD1,751 | BD | 1.75 | 1 | 130
| BD1,8751 | BD | 1.875 | 1 | 130
| BD21 | BD | 2 | 1 | 130
| BD2,251 | BD | 2.25 | 1 | 130
| BD2,51 | BD | 2.5 | 1 | 130
| BD2,751 | BD | 2.75 | 1 | 130
| BD31 | BD | 3 | 1 | 130
| BD3,251 | BD | 3.25 | 1 | 130
| BD3,51 | BD | 3.5 | 1 | 130
| BD3,751 | BD | 3.75 | 1 | 130
| BD41 | BD | 4 | 1 | 130
| L430,251 | L43 | 0.25 | 1 | 105
| L430,31251 | L43 | 0.3125 | 1 | 105
| L430,3751 | L43 | 0.375 | 1 | 105
| L430,43751 | L43 | 0.4375 | 1 | 105
| L430,51 | L43 | 0.5 | 1 | 105
| L430,56251 | L43 | 0.5625 | 1 | 105
| L430,6251 | L43 | 0.625 | 1 | 105
| L430,751 | L43 | 0.75 | 1 | 105
| L430,8751 | L43 | 0.875 | 1 | 105
| L4311 | L43 | 1 | 1 | 105
| L431,1251 | L43 | 1.125 | 1 | 105
| L431,251 | L43 | 1.25 | 1 | 105
| L431,3751 | L43 | 1.375 | 1 | 105
| L431,51 | L43 | 1.5 | 1 | 105
| L431,6251 | L43 | 1.625 | 1 | 105
| L431,751 | L43 | 1.75 | 1 | 105
| L431,8751 | L43 | 1.875 | 1 | 105
| L4321 | L43 | 2 | 1 | 105
| L432,251 | L43 | 2.25 | 1 | 105
| L432,51 | L43 | 2.5 | 1 | 105
| L432,751 | L43 | 2.75 | 1 | 105
| L4331 | L43 | 3 | 1 | 105
| L433,251 | L43 | 3.25 | 1 | 105
| L433,51 | L43 | 3.5 | 1 | 105
| L433,751 | L43 | 3.75 | 1 | 105
| L4341 | L43 | 4 | 1 | 105
| L70,251 | L7 | 0.25 | 1 | 105
| L70,31251 | L7 | 0.3125 | 1 | 105
| L70,3751 | L7 | 0.375 | 1 | 105
| L70,43751 | L7 | 0.4375 | 1 | 105
| L70,51 | L7 | 0.5 | 1 | 105
| L70,56251 | L7 | 0.5625 | 1 | 105
| L70,6251 | L7 | 0.625 | 1 | 105
| L70,751 | L7 | 0.75 | 1 | 105
| L70,8751 | L7 | 0.875 | 1 | 105
| L711 | L7 | 1 | 1 | 105
| L71,1251 | L7 | 1.125 | 1 | 105
| L71,251 | L7 | 1.25 | 1 | 105
| L71,3751 | L7 | 1.375 | 1 | 105
| L71,51 | L7 | 1.5 | 1 | 105
| L71,6251 | L7 | 1.625 | 1 | 105
| L71,751 | L7 | 1.75 | 1 | 105
| L71,8751 | L7 | 1.875 | 1 | 105
| L721 | L7 | 2 | 1 | 105
| L72,251 | L7 | 2.25 | 1 | 105
| L72,51 | L7 | 2.5 | 1 | 105
| L72,751 | L7 | 2.75 | 1 | 105
| L731 | L7 | 3 | 1 | 105
| L73,251 | L7 | 3.25 | 1 | 105
| L73,51 | L7 | 3.5 | 1 | 105
| L73,751 | L7 | 3.75 | 1 | 105
| L741 | L7 | 4 | 1 | 105
| L7A0,251 | L7A | 0.25 | 1 | 105
| L7A0,31251 | L7A | 0.3125 | 1 | 105
| L7A0,3751 | L7A | 0.375 | 1 | 105
| L7A0,43751 | L7A | 0.4375 | 1 | 105
| L7A0,51 | L7A | 0.5 | 1 | 105
| L7A0,56251 | L7A | 0.5625 | 1 | 105
| L7A0,6251 | L7A | 0.625 | 1 | 105
| L7A0,751 | L7A | 0.75 | 1 | 105
| L7A0,8751 | L7A | 0.875 | 1 | 105
| L7A11 | L7A | 1 | 1 | 105
| L7A1,1251 | L7A | 1.125 | 1 | 105
| L7A1,251 | L7A | 1.25 | 1 | 105
| L7A1,3751 | L7A | 1.375 | 1 | 105
| L7A1,51 | L7A | 1.5 | 1 | 105
| L7A1,6251 | L7A | 1.625 | 1 | 105
| L7A1,751 | L7A | 1.75 | 1 | 105
| L7A1,8751 | L7A | 1.875 | 1 | 105
| L7A21 | L7A | 2 | 1 | 105
| L7A2,251 | L7A | 2.25 | 1 | 105
| L7A2,51 | L7A | 2.5 | 1 | 105
| L7A2,751 | L7A | 2.75 | 1 | 105
| L7A31 | L7A | 3 | 1 | 105
| L7A3,251 | L7A | 3.25 | 1 | 105
| L7A3,51 | L7A | 3.5 | 1 | 105
| L7A3,751 | L7A | 3.75 | 1 | 105
| L7A41 | L7A | 4 | 1 | 105
| L7B0,251 | L7B | 0.25 | 1 | 105
| L7B0,31251 | L7B | 0.3125 | 1 | 105
| L7B0,3751 | L7B | 0.375 | 1 | 105
| L7B0,43751 | L7B | 0.4375 | 1 | 105
| L7B0,51 | L7B | 0.5 | 1 | 105
| L7B0,56251 | L7B | 0.5625 | 1 | 105
| L7B0,6251 | L7B | 0.625 | 1 | 105
| L7B0,751 | L7B | 0.75 | 1 | 105
| L7B0,8751 | L7B | 0.875 | 1 | 105
| L7B11 | L7B | 1 | 1 | 105
| L7B1,1251 | L7B | 1.125 | 1 | 105
| L7B1,251 | L7B | 1.25 | 1 | 105
| L7B1,3751 | L7B | 1.375 | 1 | 105
| L7B1,51 | L7B | 1.5 | 1 | 105
| L7B1,6251 | L7B | 1.625 | 1 | 105
| L7B1,751 | L7B | 1.75 | 1 | 105
| L7B1,8751 | L7B | 1.875 | 1 | 105
| L7B21 | L7B | 2 | 1 | 105
| L7B2,251 | L7B | 2.25 | 1 | 105
| L7B2,51 | L7B | 2.5 | 1 | 105
| L7B2,751 | L7B | 2.75 | 1 | 105
| L7B31 | L7B | 3 | 1 | 105
| L7B3,251 | L7B | 3.25 | 1 | 105
| L7B3,51 | L7B | 3.5 | 1 | 105
| L7B3,751 | L7B | 3.75 | 1 | 105
| L7B41 | L7B | 4 | 1 | 105
| L7C0,251 | L7C | 0.25 | 1 | 105
| L7C0,31251 | L7C | 0.3125 | 1 | 105
| L7C0,3751 | L7C | 0.375 | 1 | 105
| L7C0,43751 | L7C | 0.4375 | 1 | 105
| L7C0,51 | L7C | 0.5 | 1 | 105
| L7C0,56251 | L7C | 0.5625 | 1 | 105
| L7C0,6251 | L7C | 0.625 | 1 | 105
| L7C0,751 | L7C | 0.75 | 1 | 105
| L7C0,8751 | L7C | 0.875 | 1 | 105
| L7C11 | L7C | 1 | 1 | 105
| L7C1,1251 | L7C | 1.125 | 1 | 105
| L7C1,251 | L7C | 1.25 | 1 | 105
| L7C1,3751 | L7C | 1.375 | 1 | 105
| L7C1,51 | L7C | 1.5 | 1 | 105
| L7C1,6251 | L7C | 1.625 | 1 | 105
| L7C1,751 | L7C | 1.75 | 1 | 105
| L7C1,8751 | L7C | 1.875 | 1 | 105
| L7C21 | L7C | 2 | 1 | 105
| L7C2,251 | L7C | 2.25 | 1 | 105
| L7C2,51 | L7C | 2.5 | 1 | 105
| L7C2,751 | L7C | 2.75 | 1 | 105
| L7C31 | L7C | 3 | 1 | 105
| L7C3,251 | L7C | 3.25 | 1 | 105
| L7C3,51 | L7C | 3.5 | 1 | 105
| L7C3,751 | L7C | 3.75 | 1 | 105
| L7C41 | L7C | 4 | 1 | 105
| L7M0,251 | L7M | 0.25 | 1 | 80
| L7M0,31251 | L7M | 0.3125 | 1 | 80
| L7M0,3751 | L7M | 0.375 | 1 | 80
| L7M0,43751 | L7M | 0.4375 | 1 | 80
| L7M0,51 | L7M | 0.5 | 1 | 80
| L7M0,56251 | L7M | 0.5625 | 1 | 80
| L7M0,6251 | L7M | 0.625 | 1 | 80
| L7M0,751 | L7M | 0.75 | 1 | 80
| L7M0,8751 | L7M | 0.875 | 1 | 80
| L7M11 | L7M | 1 | 1 | 80
| L7M1,1251 | L7M | 1.125 | 1 | 80
| L7M1,251 | L7M | 1.25 | 1 | 80
| L7M1,3751 | L7M | 1.375 | 1 | 80
| L7M1,51 | L7M | 1.5 | 1 | 80
| L7M1,6251 | L7M | 1.625 | 1 | 80
| L7M1,751 | L7M | 1.75 | 1 | 80
| L7M1,8751 | L7M | 1.875 | 1 | 80
| L7M21 | L7M | 2 | 1 | 80
| L7M2,251 | L7M | 2.25 | 1 | 80
| L7M2,51 | L7M | 2.5 | 1 | 80
| L7M2,751 | L7M | 2.75 | 1 | 80
| L7M31 | L7M | 3 | 1 | 80
| L7M3,251 | L7M | 3.25 | 1 | 80
| L7M3,51 | L7M | 3.5 | 1 | 80
| L7M3,751 | L7M | 3.75 | 1 | 80
| L7M41 | L7M | 4 | 1 | 80
| 3.60,251 | 3.6 | 0.25 | 1 | 26.1068 | 0.25 | 1 | 26.1068
| 3.60,31251 | 3.6 | 0.3125 | 1 | 26.1068 | 0.3125 | 1 | 26.1068
| 3.60,3751 | 3.6 | 0.375 | 1 | 26.1068 | 0.375 | 1 | 26.1068
| 3.60,43751 | 3.6 | 0.4375 | 1 | 26.1068 | 0.4375 | 1 | 26.1068
| 3.60,51 | 3.6 | 0.5 | 1 | 26.1068 | 0.5 | 1 | 26.1068
| 3.60,56251 | 3.6 | 0.5625 | 1 | 26.1068 | 0.5625 | 1 | 26.1068
| 3.60,6251 | 3.6 | 0.625 | 1 | 26.1068 | 0.625 | 1 | 26.1068
| 3.60,751 | 3.6 | 0.75 | 1 | 26.1068 | 0.75 | 1 | 26.1068
| 3.60,8751 | 3.6 | 0.875 | 1 | 26.1068 | 0.875 | 1 | 26.1068
| 3.611 | 3.6 | 1 | 1 | 26.1068 | 1 | 1 | 26.1068
| 3.61,1251 | 3.6 | 1.125 | 1 | 26.1068 | 1.125 | 1 | 26.1068
| 3.61,251 | 3.6 | 1.25 | 1 | 26.1068 | 1.25 | 1 | 26.1068
| 3.61,3751 | 3.6 | 1.375 | 1 | 26.1068 | 1.375 | 1 | 26.1068
| 3.61,51 | 3.6 | 1.5 | 1 | 26.1068 | 1.5 | 1 | 26.1068
| 3.61,6251 | 3.6 | 1.625 | 1 | 26.1068 | 1.625 | 1 | 26.1068
| 3.61,751 | 3.6 | 1.75 | 1 | 26.1068 | 1.75 | 1 | 26.1068
| 3.61,8751 | 3.6 | 1.875 | 1 | 26.1068 | 1.875 | 1 | 26.1068
| 3.621 | 3.6 | 2 | 1 | 26.1068 | 2 | 1 | 26.1068
| 3.62,251 | 3.6 | 2.25 | 1 | 26.1068 | 2.25 | 1 | 26.1068
| 3.62,51 | 3.6 | 2.5 | 1 | 26.1068 | 2.5 | 1 | 26.1068
| 3.62,751 | 3.6 | 2.75 | 1 | 26.1068 | 2.75 | 1 | 26.1068
| 3.631 | 3.6 | 3 | 1 | 26.1068 | 3 | 1 | 26.1068
| 3.63,251 | 3.6 | 3.25 | 1 | 26.1068 | 3.25 | 1 | 26.1068
| 3.63,51 | 3.6 | 3.5 | 1 | 26.1068 | 3.5 | 1 | 26.1068
| 3.63,751 | 3.6 | 3.75 | 1 | 26.1068 | 3.75 | 1 | 26.1068
| 3.641 | 3.6 | 4 | 1 | 26.1068 | 4 | 1 | 26.1068
| 4.60,251 | 4.6 | 0.25 | 1 | 34.8091
| 4.60,31251 | 4.6 | 0.3125 | 1 | 34.8091
| 4.60,3751 | 4.6 | 0.375 | 1 | 34.8091
| 4.60,43751 | 4.6 | 0.4375 | 1 | 34.8091
| 4.60,51 | 4.6 | 0.5 | 1 | 34.8091
| 4.60,56251 | 4.6 | 0.5625 | 1 | 34.8091
| 4.60,6251 | 4.6 | 0.625 | 1 | 34.8091
| 4.60,751 | 4.6 | 0.75 | 1 | 34.8091
| 4.60,8751 | 4.6 | 0.875 | 1 | 34.8091
| 4.611 | 4.6 | 1 | 1 | 34.8091
| 4.61,1251 | 4.6 | 1.125 | 1 | 34.8091
| 4.61,251 | 4.6 | 1.25 | 1 | 34.8091
| 4.61,3751 | 4.6 | 1.375 | 1 | 34.8091
| 4.61,51 | 4.6 | 1.5 | 1 | 34.8091
| 4.61,6251 | 4.6 | 1.625 | 1 | 34.8091
| 4.61,751 | 4.6 | 1.75 | 1 | 34.8091
| 4.61,8751 | 4.6 | 1.875 | 1 | 34.8091
| 4.621 | 4.6 | 2 | 1 | 34.8091
| 4.62,251 | 4.6 | 2.25 | 1 | 34.8091
| 4.62,51 | 4.6 | 2.5 | 1 | 34.8091
| 4.62,751 | 4.6 | 2.75 | 1 | 34.8091
| 4.631 | 4.6 | 3 | 1 | 34.8091
| 4.63,251 | 4.6 | 3.25 | 1 | 34.8091
| 4.63,51 | 4.6 | 3.5 | 1 | 34.8091
| 4.63,751 | 4.6 | 3.75 | 1 | 34.8091
| 4.641 | 4.6 | 4 | 1 | 34.8091
| 4.80,251 | 4.8 | 0.25 | 1 | 46.4121
| 4.80,31251 | 4.8 | 0.3125 | 1 | 46.4121
| 4.80,3751 | 4.8 | 0.375 | 1 | 46.4121
| 4.80,43751 | 4.8 | 0.4375 | 1 | 46.4121
| 4.80,51 | 4.8 | 0.5 | 1 | 46.4121
| 4.80,56251 | 4.8 | 0.5625 | 1 | 46.4121
| 4.80,6251 | 4.8 | 0.625 | 1 | 46.4121
| 4.80,751 | 4.8 | 0.75 | 1 | 46.4121
| 4.80,8751 | 4.8 | 0.875 | 1 | 46.4121
| 4.811 | 4.8 | 1 | 1 | 46.4121
| 4.81,1251 | 4.8 | 1.125 | 1 | 46.4121
| 4.81,251 | 4.8 | 1.25 | 1 | 46.4121
| 4.81,3751 | 4.8 | 1.375 | 1 | 46.4121
| 4.81,51 | 4.8 | 1.5 | 1 | 46.4121
| 4.81,6251 | 4.8 | 1.625 | 1 | 46.4121
| 4.81,751 | 4.8 | 1.75 | 1 | 46.4121
| 4.81,8751 | 4.8 | 1.875 | 1 | 46.4121
| 4.821 | 4.8 | 2 | 1 | 46.4121
| 4.82,251 | 4.8 | 2.25 | 1 | 46.4121
| 4.82,51 | 4.8 | 2.5 | 1 | 46.4121
| 4.82,751 | 4.8 | 2.75 | 1 | 46.4121
| 4.831 | 4.8 | 3 | 1 | 46.4121
| 4.83,251 | 4.8 | 3.25 | 1 | 46.4121
| 4.83,51 | 4.8 | 3.5 | 1 | 46.4121
| 4.83,751 | 4.8 | 3.75 | 1 | 46.4121
| 4.841 | 4.8 | 4 | 1 | 46.4121
| 5.60,251 | 5.6 | 0.25 | 1 | 43.5113
| 5.60,31251 | 5.6 | 0.3125 | 1 | 43.5113
| 5.60,3751 | 5.6 | 0.375 | 1 | 43.5113
| 5.60,43751 | 5.6 | 0.4375 | 1 | 43.5113
| 5.60,51 | 5.6 | 0.5 | 1 | 43.5113
| 5.60,56251 | 5.6 | 0.5625 | 1 | 43.5113
| 5.60,6251 | 5.6 | 0.625 | 1 | 43.5113
| 5.60,751 | 5.6 | 0.75 | 1 | 43.5113
| 5.60,8751 | 5.6 | 0.875 | 1 | 43.5113
| 5.611 | 5.6 | 1 | 1 | 43.5113
| 5.61,1251 | 5.6 | 1.125 | 1 | 43.5113
| 5.61,251 | 5.6 | 1.25 | 1 | 43.5113
| 5.61,3751 | 5.6 | 1.375 | 1 | 43.5113
| 5.61,51 | 5.6 | 1.5 | 1 | 43.5113
| 5.61,6251 | 5.6 | 1.625 | 1 | 43.5113
| 5.61,751 | 5.6 | 1.75 | 1 | 43.5113
| 5.61,8751 | 5.6 | 1.875 | 1 | 43.5113
| 5.621 | 5.6 | 2 | 1 | 43.5113
| 5.62,251 | 5.6 | 2.25 | 1 | 43.5113
| 5.62,51 | 5.6 | 2.5 | 1 | 43.5113
| 5.62,751 | 5.6 | 2.75 | 1 | 43.5113
| 5.631 | 5.6 | 3 | 1 | 43.5113
| 5.63,251 | 5.6 | 3.25 | 1 | 43.5113
| 5.63,51 | 5.6 | 3.5 | 1 | 43.5113
| 5.63,751 | 5.6 | 3.75 | 1 | 43.5113
| 5.641 | 5.6 | 4 | 1 | 43.5113
| 5.80,251 | 5.8 | 0.25 | 1 | 58.0151
| 5.80,31251 | 5.8 | 0.3125 | 1 | 58.0151
| 5.80,3751 | 5.8 | 0.375 | 1 | 58.0151
| 5.80,43751 | 5.8 | 0.4375 | 1 | 58.0151
| 5.80,51 | 5.8 | 0.5 | 1 | 58.0151
| 5.80,56251 | 5.8 | 0.5625 | 1 | 58.0151
| 5.80,6251 | 5.8 | 0.625 | 1 | 58.0151
| 5.80,751 | 5.8 | 0.75 | 1 | 58.0151
| 5.80,8751 | 5.8 | 0.875 | 1 | 58.0151
| 5.811 | 5.8 | 1 | 1 | 58.0151
| 5.81,1251 | 5.8 | 1.125 | 1 | 58.0151
| 5.81,251 | 5.8 | 1.25 | 1 | 58.0151
| 5.81,3751 | 5.8 | 1.375 | 1 | 58.0151
| 5.81,51 | 5.8 | 1.5 | 1 | 58.0151
| 5.81,6251 | 5.8 | 1.625 | 1 | 58.0151
| 5.81,751 | 5.8 | 1.75 | 1 | 58.0151
| 5.81,8751 | 5.8 | 1.875 | 1 | 58.0151
| 5.821 | 5.8 | 2 | 1 | 58.0151
| 5.82,251 | 5.8 | 2.25 | 1 | 58.0151
| 5.82,51 | 5.8 | 2.5 | 1 | 58.0151
| 5.82,751 | 5.8 | 2.75 | 1 | 58.0151
| 5.831 | 5.8 | 3 | 1 | 58.0151
| 5.83,251 | 5.8 | 3.25 | 1 | 58.0151
| 5.83,51 | 5.8 | 3.5 | 1 | 58.0151
| 5.83,751 | 5.8 | 3.75 | 1 | 58.0151
| 5.841 | 5.8 | 4 | 1 | 58.0151
| 6.80,251 | 6.8 | 0.25 | 1 | 69.6181
| 6.80,31251 | 6.8 | 0.3125 | 1 | 69.6181
| 6.80,3751 | 6.8 | 0.375 | 1 | 69.6181
| 6.80,43751 | 6.8 | 0.4375 | 1 | 69.6181
| 6.80,51 | 6.8 | 0.5 | 1 | 69.6181
| 6.80,56251 | 6.8 | 0.5625 | 1 | 69.6181
| 6.80,6251 | 6.8 | 0.625 | 1 | 69.6181
| 6.80,751 | 6.8 | 0.75 | 1 | 69.6181
| 6.80,8751 | 6.8 | 0.875 | 1 | 69.6181
| 6.811 | 6.8 | 1 | 1 | 69.6181
| 6.81,1251 | 6.8 | 1.125 | 1 | 69.6181
| 6.81,251 | 6.8 | 1.25 | 1 | 69.6181
| 6.81,3751 | 6.8 | 1.375 | 1 | 69.6181
| 6.81,51 | 6.8 | 1.5 | 1 | 69.6181
| 6.81,6251 | 6.8 | 1.625 | 1 | 69.6181
| 6.81,751 | 6.8 | 1.75 | 1 | 69.6181
| 6.81,8751 | 6.8 | 1.875 | 1 | 69.6181
| 6.821 | 6.8 | 2 | 1 | 69.6181
| 6.82,251 | 6.8 | 2.25 | 1 | 69.6181
| 6.82,51 | 6.8 | 2.5 | 1 | 69.6181
| 6.82,751 | 6.8 | 2.75 | 1 | 69.6181
| 6.831 | 6.8 | 3 | 1 | 69.6181
| 6.83,251 | 6.8 | 3.25 | 1 | 69.6181
| 6.83,51 | 6.8 | 3.5 | 1 | 69.6181
| 6.83,751 | 6.8 | 3.75 | 1 | 69.6181
| 6.841 | 6.8 | 4 | 1 | 69.6181
| 8.80,251 | 8.8 | 0.25 | 1 | 92.8242
| 8.80,31251 | 8.8 | 0.3125 | 1 | 92.8242
| 8.80,3751 | 8.8 | 0.375 | 1 | 92.8242
| 8.80,43751 | 8.8 | 0.4375 | 1 | 92.8242
| 8.80,51 | 8.8 | 0.5 | 1 | 92.8242
| 8.80,56251 | 8.8 | 0.5625 | 1 | 92.8242
| 8.80,6251 | 8.8 | 0.625 | 1 | 92.8242
| 8.80,751 | 8.8 | 0.75 | 1 | 92.8242
| 8.80,8751 | 8.8 | 0.875 | 1 | 92.8242
| 8.811 | 8.8 | 1 | 1 | 92.8242
| 8.81,1251 | 8.8 | 1.125 | 1 | 92.8242
| 8.81,251 | 8.8 | 1.25 | 1 | 92.8242
| 8.81,3751 | 8.8 | 1.375 | 1 | 92.8242
| 8.81,51 | 8.8 | 1.5 | 1 | 92.8242
| 8.81,6251 | 8.8 | 1.625 | 1 | 92.8242
| 8.81,751 | 8.8 | 1.75 | 1 | 92.8242
| 8.81,8751 | 8.8 | 1.875 | 1 | 92.8242
| 8.821 | 8.8 | 2 | 1 | 92.8242
| 8.82,251 | 8.8 | 2.25 | 1 | 92.8242
| 8.82,51 | 8.8 | 2.5 | 1 | 92.8242
| 8.82,751 | 8.8 | 2.75 | 1 | 92.8242
| 8.831 | 8.8 | 3 | 1 | 92.8242
| 8.83,251 | 8.8 | 3.25 | 1 | 92.8242
| 8.83,51 | 8.8 | 3.5 | 1 | 92.8242
| 8.83,751 | 8.8 | 3.75 | 1 | 92.8242
| 8.841 | 8.8 | 4 | 1 | 92.8242
| 9.80,251 | 9.8 | 0.25 | 1 | 104.4272
| 9.80,31251 | 9.8 | 0.3125 | 1 | 104.4272
| 9.80,3751 | 9.8 | 0.375 | 1 | 104.4272
| 9.80,43751 | 9.8 | 0.4375 | 1 | 104.4272
| 9.80,51 | 9.8 | 0.5 | 1 | 104.4272
| 9.80,56251 | 9.8 | 0.5625 | 1 | 104.4272
| 9.80,6251 | 9.8 | 0.625 | 1 | 104.4272
| 9.80,751 | 9.8 | 0.75 | 1 | 104.4272
| 9.80,8751 | 9.8 | 0.875 | 1 | 104.4272
| 9.811 | 9.8 | 1 | 1 | 104.4272
| 9.81,1251 | 9.8 | 1.125 | 1 | 104.4272
| 9.81,251 | 9.8 | 1.25 | 1 | 104.4272
| 9.81,3751 | 9.8 | 1.375 | 1 | 104.4272
| 9.81,51 | 9.8 | 1.5 | 1 | 104.4272
| 9.81,6251 | 9.8 | 1.625 | 1 | 104.4272
| 9.81,751 | 9.8 | 1.75 | 1 | 104.4272
| 9.81,8751 | 9.8 | 1.875 | 1 | 104.4272
| 9.821 | 9.8 | 2 | 1 | 104.4272
| 9.82,251 | 9.8 | 2.25 | 1 | 104.4272
| 9.82,51 | 9.8 | 2.5 | 1 | 104.4272
| 9.82,751 | 9.8 | 2.75 | 1 | 104.4272
| 9.831 | 9.8 | 3 | 1 | 104.4272
| 9.83,251 | 9.8 | 3.25 | 1 | 104.4272
| 9.83,51 | 9.8 | 3.5 | 1 | 104.4272
| 9.83,751 | 9.8 | 3.75 | 1 | 104.4272
| 9.841 | 9.8 | 4 | 1 | 104.4272
| 10.90,251 | 10.9 | 0.25 | 1 | 130.534
| 10.90,31251 | 10.9 | 0.3125 | 1 | 130.534
| 10.90,3751 | 10.9 | 0.375 | 1 | 130.534
| 10.90,43751 | 10.9 | 0.4375 | 1 | 130.534
| 10.90,51 | 10.9 | 0.5 | 1 | 130.534
| 10.90,56251 | 10.9 | 0.5625 | 1 | 130.534
| 10.90,6251 | 10.9 | 0.625 | 1 | 130.534
| 10.90,751 | 10.9 | 0.75 | 1 | 130.534
| 10.90,8751 | 10.9 | 0.875 | 1 | 130.534
| 10.911 | 10.9 | 1 | 1 | 130.534
| 10.91,1251 | 10.9 | 1.125 | 1 | 130.534
| 10.91,251 | 10.9 | 1.25 | 1 | 130.534
| 10.91,3751 | 10.9 | 1.375 | 1 | 130.534
| 10.91,51 | 10.9 | 1.5 | 1 | 130.534
| 10.91,6251 | 10.9 | 1.625 | 1 | 130.534
| 10.91,751 | 10.9 | 1.75 | 1 | 130.534
| 10.91,8751 | 10.9 | 1.875 | 1 | 130.534
| 10.921 | 10.9 | 2 | 1 | 130.534
| 10.92,251 | 10.9 | 2.25 | 1 | 130.534
| 10.92,51 | 10.9 | 2.5 | 1 | 130.534
| 10.92,751 | 10.9 | 2.75 | 1 | 130.534
| 10.931 | 10.9 | 3 | 1 | 130.534
| 10.93,251 | 10.9 | 3.25 | 1 | 130.534
| 10.93,51 | 10.9 | 3.5 | 1 | 130.534
| 10.93,751 | 10.9 | 3.75 | 1 | 130.534
| 10.941 | 10.9 | 4 | 1 | 130.534
| 12.90,251 | 12.9 | 0.25 | 1 | 156.6408
| 12.90,31251 | 12.9 | 0.3125 | 1 | 156.6408
| 12.90,3751 | 12.9 | 0.375 | 1 | 156.6408
| 12.90,43751 | 12.9 | 0.4375 | 1 | 156.6408
| 12.90,51 | 12.9 | 0.5 | 1 | 156.6408
| 12.90,56251 | 12.9 | 0.5625 | 1 | 156.6408
| 12.90,6251 | 12.9 | 0.625 | 1 | 156.6408
| 12.90,751 | 12.9 | 0.75 | 1 | 156.6408
| 12.90,8751 | 12.9 | 0.875 | 1 | 156.6408
| 12.911 | 12.9 | 1 | 1 | 156.6408
| 12.91,1251 | 12.9 | 1.125 | 1 | 156.6408
| 12.91,251 | 12.9 | 1.25 | 1 | 156.6408
| 12.91,3751 | 12.9 | 1.375 | 1 | 156.6408
| 12.91,51 | 12.9 | 1.5 | 1 | 156.6408
| 12.91,6251 | 12.9 | 1.625 | 1 | 156.6408
| 12.91,751 | 12.9 | 1.75 | 1 | 156.6408
| 12.91,8751 | 12.9 | 1.875 | 1 | 156.6408
| 12.921 | 12.9 | 2 | 1 | 156.6408
| 12.92,251 | 12.9 | 2.25 | 1 | 156.6408
| 12.92,51 | 12.9 | 2.5 | 1 | 156.6408
| 12.92,751 | 12.9 | 2.75 | 1 | 156.6408
| 12.931 | 12.9 | 3 | 1 | 156.6408
| 12.93,251 | 12.9 | 3.25 | 1 | 156.6408
| 12.93,51 | 12.9 | 3.5 | 1 | 156.6408
| 12.93,751 | 12.9 | 3.75 | 1 | 156.6408
| 12.941 | 12.9 | 4 | 1 | 156.6408
| A2/A4-700,251 | A2/A4-70 | 0.25 | 1 | 65.267
| A2/A4-700,31251 | A2/A4-70 | 0.3125 | 1 | 65.267
| A2/A4-700,3751 | A2/A4-70 | 0.375 | 1 | 65.267
| A2/A4-700,43751 | A2/A4-70 | 0.4375 | 1 | 65.267
| A2/A4-700,51 | A2/A4-70 | 0.5 | 1 | 65.267
| A2/A4-700,56251 | A2/A4-70 | 0.5625 | 1 | 65.267
| A2/A4-700,6251 | A2/A4-70 | 0.625 | 1 | 65.267
| A2/A4-700,751 | A2/A4-70 | 0.75 | 1 | 65.267
| A2/A4-700,8751 | A2/A4-70 | 0.875 | 1 | 65.267
| A2/A4-7011 | A2/A4-70 | 1 | 1 | 65.267
| A2/A4-701,1251 | A2/A4-70 | 1.125 | 1 | 65.267
| A2/A4-701,251 | A2/A4-70 | 1.25 | 1 | 65.267
| A2/A4-701,3751 | A2/A4-70 | 1.375 | 1 | 65.267
| A2/A4-701,51 | A2/A4-70 | 1.5 | 1 | 65.267
| A2/A4-701,6251 | A2/A4-70 | 1.625 | 1 | 65.267
| A2/A4-701,751 | A2/A4-70 | 1.75 | 1 | 65.267
| A2/A4-701,8751 | A2/A4-70 | 1.875 | 1 | 65.267
| A2/A4-7021 | A2/A4-70 | 2 | 1 | 65.267
| A2/A4-702,251 | A2/A4-70 | 2.25 | 1 | 65.267
| A2/A4-702,51 | A2/A4-70 | 2.5 | 1 | 65.267
| A2/A4-702,751 | A2/A4-70 | 2.75 | 1 | 65.267
| A2/A4-7031 | A2/A4-70 | 3 | 1 | 65.267
| A2/A4-703,251 | A2/A4-70 | 3.25 | 1 | 65.267
| A2/A4-703,51 | A2/A4-70 | 3.5 | 1 | 65.267
| A2/A4-703,751 | A2/A4-70 | 3.75 | 1 | 65.267
| A2/A4-7041 | A2/A4-70 | 4 | 1 | 65.267
| 25CrMo40,251 | 25CrMo4 | 0.25 | 1 | 63.8166
| 25CrMo40,31251 | 25CrMo4 | 0.3125 | 1 | 63.8166
| 25CrMo40,3751 | 25CrMo4 | 0.375 | 1 | 63.8166
| 25CrMo40,43751 | 25CrMo4 | 0.4375 | 1 | 63.8166
| 25CrMo40,51 | 25CrMo4 | 0.5 | 1 | 63.8166
| 25CrMo40,56251 | 25CrMo4 | 0.5625 | 1 | 63.8166
| 25CrMo40,6251 | 25CrMo4 | 0.625 | 1 | 63.8166
| 25CrMo40,751 | 25CrMo4 | 0.75 | 1 | 63.8166
| 25CrMo40,8751 | 25CrMo4 | 0.875 | 1 | 63.8166
| 25CrMo411 | 25CrMo4 | 1 | 1 | 63.8166
| 25CrMo41,1251 | 25CrMo4 | 1.125 | 1 | 63.8166
| 25CrMo41,251 | 25CrMo4 | 1.25 | 1 | 63.8166
| 25CrMo41,3751 | 25CrMo4 | 1.375 | 1 | 63.8166
| 25CrMo41,51 | 25CrMo4 | 1.5 | 1 | 63.8166
| 25CrMo41,6251 | 25CrMo4 | 1.625 | 1 | 63.8166
| 25CrMo41,751 | 25CrMo4 | 1.75 | 1 | 63.8166
| 25CrMo41,8751 | 25CrMo4 | 1.875 | 1 | 63.8166
| 25CrMo421 | 25CrMo4 | 2 | 1 | 63.8166
| 25CrMo42,251 | 25CrMo4 | 2.25 | 1 | 63.8166
| 25CrMo42,51 | 25CrMo4 | 2.5 | 1 | 63.8166
| 25CrMo42,751 | 25CrMo4 | 2.75 | 1 | 63.8166
| 25CrMo431 | 25CrMo4 | 3 | 1 | 63.8166
| 25CrMo43,251 | 25CrMo4 | 3.25 | 1 | 63.8166
| 25CrMo43,51 | 25CrMo4 | 3.5 | 1 | 63.8166
| 25CrMo43,751 | 25CrMo4 | 3.75 | 1 | 63.8166
| 25CrMo441 | 25CrMo4 | 4 | 1 | 63.8166
| 42CrMo40,251 | 42CrMo4 | 0.25 | 1 | 105.8775
| 42CrMo40,31251 | 42CrMo4 | 0.3125 | 1 | 105.8775
| 42CrMo40,3751 | 42CrMo4 | 0.375 | 1 | 105.8775
| 42CrMo40,43751 | 42CrMo4 | 0.4375 | 1 | 105.8775
| 42CrMo40,51 | 42CrMo4 | 0.5 | 1 | 105.8775
| 42CrMo40,56251 | 42CrMo4 | 0.5625 | 1 | 105.8775
| 42CrMo40,6251 | 42CrMo4 | 0.625 | 1 | 105.8775
| 42CrMo40,751 | 42CrMo4 | 0.75 | 1 | 105.8775
| 42CrMo40,8751 | 42CrMo4 | 0.875 | 1 | 105.8775
| 42CrMo411 | 42CrMo4 | 1 | 1 | 105.8775
| 42CrMo41,1251 | 42CrMo4 | 1.125 | 1 | 105.8775
| 42CrMo41,251 | 42CrMo4 | 1.25 | 1 | 105.8775
| 42CrMo41,3751 | 42CrMo4 | 1.375 | 1 | 105.8775
| 42CrMo41,51 | 42CrMo4 | 1.5 | 1 | 105.8775
| 42CrMo41,6251 | 42CrMo4 | 1.625 | 1 | 105.8775
| 42CrMo41,751 | 42CrMo4 | 1.75 | 1 | 105.8775
| 42CrMo41,8751 | 42CrMo4 | 1.875 | 1 | 105.8775
| 42CrMo421 | 42CrMo4 | 2 | 1 | 105.8775
| 42CrMo42,251 | 42CrMo4 | 2.25 | 1 | 105.8775
| 42CrMo42,51 | 42CrMo4 | 2.5 | 1 | 105.8775
| 42CrMo42,751 | 42CrMo4 | 2.75 | 1 | 105.8775
| 42CrMo431 | 42CrMo4 | 3 | 1 | 105.8775
| 42CrMo43,251 | 42CrMo4 | 3.25 | 1 | 105.8775
| 42CrMo43,51 | 42CrMo4 | 3.5 | 1 | 105.8775
| 42CrMo43,751 | 42CrMo4 | 3.75 | 1 | 105.8775
| 42CrMo441 | 42CrMo4 | 4 | 1 | 105.8775
| I7180,251 | I718 | 0.25 | 1 | 150
| I7180,31251 | I718 | 0.3125 | 1 | 150
| I7180,3751 | I718 | 0.375 | 1 | 150
| I7180,43751 | I718 | 0.4375 | 1 | 150
| I7180,51 | I718 | 0.5 | 1 | 150
| I7180,56251 | I718 | 0.5625 | 1 | 150
| I7180,6251 | I718 | 0.625 | 1 | 150
| I7180,751 | I718 | 0.75 | 1 | 150
| I7180,8751 | I718 | 0.875 | 1 | 150
| I71811 | I718 | 1 | 1 | 150
| I7181,1251 | I718 | 1.125 | 1 | 150
| I7181,251 | I718 | 1.25 | 1 | 150
| I7181,3751 | I718 | 1.375 | 1 | 150
| I7181,51 | I718 | 1.5 | 1 | 150
| I7181,6251 | I718 | 1.625 | 1 | 150
| I7181,751 | I718 | 1.75 | 1 | 150
| I7181,8751 | I718 | 1.875 | 1 | 150
| I71821 | I718 | 2 | 1 | 150
| I7182,251 | I718 | 2.25 | 1 | 150
| I7182,51 | I718 | 2.5 | 1 | 150
| I7182,751 | I718 | 2.75 | 1 | 150
| I71831 | I718 | 3 | 1 | 150
| I7183,251 | I718 | 3.25 | 1 | 150
| I7183,51 | I718 | 3.5 | 1 | 150
| I7183,751 | I718 | 3.75 | 1 | 150
| I71841 | I718 | 4 | 1 | 150